Specification

1.0 General

1.1 - Unit shall be Slimline ducted high efficiency ceiling module consisting of anodized aluminum frame, a galvanized back plate, 41-mm filter pack, polyurethane encapsulating sealant and dual access ports (for the adjustable model version only). Maximum module depth shall not exceed 4.73”.

1.2 - Sizes shall be as noted on drawings or other supporting materials.

2.0 Construction

2.1 - Filter housing shall be constructed of an anodized aluminum frame mated with a galvanized steel back plate. It shall be designed for installation into a T-Bar ceiling grid system.

2.2 - The media pack shall have a maximum depth of 41-mm (1.61”) and shall have an efficiency of (95%, 99.99% @ 0.3 micron, 99.9995% @ MPPS).

2.3 - Pleat spacing shall be by thermoplastic resin separators to prevent media-to-media contact and promote uniform airflow through the media pack.

2.4 - The media pack shall be completely encapsulated in a polyurethane sealant creating a rigid self-supporting pack. The sealant shall be low out gassing, fire-resistant and self-extinguishing.

2.5 - The adjustable airflow diffusion disc version is adjustable from the room side through an access port to allow balancing across multiple units throughout the clean room.  A second port, accessible from the room side, shall be provided to allow aerosol test challenge measurement or pressure drop.

2.6 - Housing shall be supplied with a (“10”, 12”) collar that includes an integral continuous raised ridge for duct side connection to air system.

2.7 - Unit shall include an epoxy-coated steel face screen with a minimum 62% open area.

3.0 Performance

3.1 - The filter shall be identified on a label indicating minimum efficiency, tested airflow and pressure drop. The unit shall be bar code serialized for individual unit identification.

3.2 - The module shall be listed by Underwriters Laboratories as UL 900.

3.3 - Manufacturer shall provide evidence of facility certification to ISO 9001:2015.

Items in parentheses ( ) require selection.

DJM12/21